SECTION 08630

PINNACLE HURRICANE METAL-FRAMED SKYLIGHTS

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

      - SUMMARY

        - This Section includes the following:

          - Metal framed Skylights

        - Related Sections may include, but are not limited to the following:

List only products, construction, and equipment included in this Project that the reader would expect to find in this Section.  Verify that Sections listed are included in this Specification and that their titles are correct.

          - Division 5 Section "Structural Steel": for steel framing.

Verify outward thrust loads with Wasco engineers where structural steel may be required for loading.

This language needs to be reviewed by structural personnel.  I would like to give some kind of guidelines for when structural curbs will be required.  Most Architects want someone else to be responsible (mainly the skylight provider) for structural requirements.

          - Division 7 Section "Joint Sealants": for sealants installed at metal-framed skylight perimeters.

          - Division 7 Flashing and Sheet Metal:  Flashing and Sheet Metal Section.

          - Division 8 Glazing: Glass and Glazing Section.

      - PERFORMANCE REQUIREMENTS

        - General:  Provide metal-framed skylights capable of withstanding loads and thermal and structural movements indicated without failure.  Failure includes the following:

          - Deflection exceeding specified limits.

          - Thermal stresses transferred to the building structure.

          - Skylight framing members transferring stresses, including those caused by thermal and structural movement, to glazing.

          - Weakening of fasteners, attachments, and other components.

        - Deflection Limits:  As follows:

          - Deflection of the entire length of framing members in direction normal to glazing plane is limited to 1/175 of clear span.

        - Structural Loads:  Provide metal-framed skylights, including anchorage, capable of withstanding the effects of the following design loads when supporting full dead loads:

          - Roof Loads

            - Concentrated Load:  250 lb applied to framing members at location that produces the most severe stress or deflection.

            - Snow Loads:  ______________ (Insert job specific requirements)

            - Roof Loads:   ______________ (Insert job specific requirements)

            - Wind Loads:   ______________ (Insert job specific requirements)

        - Structural Performance:  Provide metal-framed skylights, including anchorage, capable of withstanding test pressure indicated without material and deflection failures and permanent deformation of structural members exceeding 0.2 percent of span when tested according to ASTM E 330.

          - Large Missile Impact Resistance: Insulated glass or laminated glass glazed skylight system must meet the requirements of Protocol TAS-201-94.

          - Static Air Pressure / Structural Loads: Insulated glass or laminated glass glazed skylight system must meet a Design Pressure of +/- 80 PSF when tested per Protocol TAS-202-94.

          - Cyclic Wind Pressure Loading: Insulated glass or laminated glass glazed skylight system must meet a Design Pressure of +/- 80 PSF when tested per Protocol TAS-203-94.

This language needs to be reviewed by structural personnel.  If there are no instances where Wasco products would be used in hurricane areas, this requirement could be omitted.  Also I am not sure what seismic requirements would be required.

In hurricane-prone areas, authorities having jurisdiction may require debris-impact and cyclic-pressure testing for glazed assemblies.  If required, insert hurricane-resistance testing requirements; verify requirements of authorities having jurisdiction.

Insert seismic testing requirements, if any.

        - Thermal Movement:  Provide metal-framed skylights that allow for thermal movements resulting from the following maximum change (range) in ambient temperatures by preventing buckling, sealant failure, and other detrimental effects.

          - Temperature Change (Range):  100 deg F.

        - Air Infiltration:  Provide metal-framed skylights with maximum air leakage of 0.06 cfm/sq. ft. (0.03 L/s per sq. m) of surface when tested according to ASTM E 283 at a minimum static-air-pressure differential of 6.24lb/sq. ft. (300 Pa).

        - Water Penetration:  Provide metal-framed skylights that do not evidence water penetration when tested according to ASTM E 331 at a minimum differential static pressure of 12 lbs/sq. ft. (584 Pa).

      - SUBMITTALS

        - Product Data:  Include construction details, material descriptions, dimensions and profiles of components, and finishes for metal-framed skylights.

        - Shop Drawings:  For metal-framed skylights.  Include plans, elevations, sections, details, and attachments to other work as required.

I need some guidance here as to how Wasco provides engineering on submittals.

Retain subparagraph below along with "Professional Engineer Qualifications" Paragraph in "Quality Assurance" Article.  Delete or modify below if Architect assumes or is required by law to assume design responsibility.

        - Samples for Initial Selection:  Manufacturer's color charts consisting of sections of units showing the full range of colors available for factory-finished aluminum.

Need some help here as to what kind of samples are typically submitted.

Delete paragraph above if colors are preselected and specified or scheduled.  Retain paragraph below with or without above.

        - Samples for Verification:  Provide 12-inch long sections of extrusions or formed shapes in same thickness and material indicated for the Work.  Mill finished sampler to be provided on piece of 2”x3” aluminum sheet.

Are there any certified installers recommended by Wasco?

Retain paragraph below if "Installer Qualifications" Paragraph is retained in "Quality Assurance" Article.

        - Installer Certificates:  If required, signed by manufacturer certifying that installers comply with requirements.

        - Product Test Reports:  From a qualified testing agency indicating skylights comply with requirements, based on comprehensive testing of current products.

Retain below if Contractor engages agency performing field tests.

      - QUALITY ASSURANCE

I need some guidance here as to how Wasco provides engineering on submittals.

        - Installer Qualifications:  An experienced installer who has specialized in installing metal-framed skylights similar to those indicated for this Project and who is acceptable to manufacturer.

Delete paragraph below if Contractor is not required to engage the services of a qualified professional engineer in "Submittals" Article.

        - Professional Engineer Qualifications:  A professional engineer who is experienced in providing engineering services of the kind indicated.  Engineering services are defined as those performed for installations of skylights that are similar to those indicated for this Project in material, design, and extent.

Retain paragraph below if Contractor or manufacturer selects testing agency.

        - Testing Agency Qualifications:  An independent approved Miami/Dade Certified testing agency with the experience and capability to conduct the testing indicated, as documented according to ASTM E 548 and TAS-201, 202 and 203.

Delete paragraph below if not required.

        - Delete paragraph below if not required.  If retaining, indicate location, size, and other details of mockups on Drawings or by inserts.  Revise wording if only one mockup is required.

Delete paragraph below if work of this Section is not extensive or complex enough to justify a preinstallation conference.  If retaining, coordinate with Division 1 Section "Project Meetings."

Retain paragraph above if requirements in Division 1 Section are adequate for Project.  Retain paragraph below if additional requirements are necessary; include information about conference.  Identify specific participants not mentioned in Division 1.

        - Pre-installation Conference:  When required, conduct conference at Project site to comply with requirements in Division 1 Section "Project Meetings."  Review methods and procedures related to metal-framed skylights including, but not limited to, the following:

Delete subparagraphs below if not required.  If retaining, revise to include product-specific requirements.  Insert additional requirements to suit Project.

          - Inspect and discuss condition of substrate and other preparatory work performed by other trades.

          - Review structural load limitations.

          - Review skylight curb structural requirements.

          - Review and finalize construction schedule and verify availability of materials, Installer's personnel, equipment, and facilities needed to make progress and avoid delays.

Coordinate subparagraph below with Division 1 Section "Quality Control" and with "Field Quality Control" Article in this Section.  Expand requirements to suit Project.

          - Review required field testing procedures.

          - Review weather and forecasted weather conditions and procedures for unfavorable conditions.

          - Review protection of adjacent roof areas.

Delete below if no field-installed structural sealant.

          - Review preparation and other requirements for installing structural silicone sealant.

Insert agenda items below not listed in Division 1 Section "Project Meetings."

      - PROJECT CONDITIONS

        - Field Measurements:  Where metal-framed skylights are indicated to fit to other construction, verify dimensions of other construction by field measurements before fabrication and indicate measurements on Shop Drawings.  Coordinate fabrication schedule with construction progress to avoid delaying the Work.

Delete below if not allowed.

          - Established Dimensions:  Where field measurements cannot be made without delaying the Work, establish dimensions and proceed with fabricating skylights without field measurements.  Coordinate construction to ensure that actual dimensions correspond to established dimensions.

      - WARRANTY

- Warranty: Written warranty, executed by manufacturer agreeing to repair or replace components of metal-framed skylights that fail in materials or workmanship within specified warranty period. Failures include, but are not limited to, the following:

  - Structural failures.

  - Failure of systems to meet performance requirements.

  - Deterioration of metals, metal finishes, and other materials beyond normal weathering.

  - Water leakage; defined as uncontrolled water appearing on normally exposed interior surfaces of skylights from sources other than condensation, resulting from defects in skylight materials or workmanship. (Water controlled by flashing and gutters and drained back to the exterior and that cannot damage adjacent materials or finishes is not water leakage). Water leakage resulting from improper installations not part of this warranty.

  - Warranty Period: 5 years from date of shipment from the manufacturer.

- Finish Warranty:  (EDIT AS REQUIRED BASED ON FINISH) Provide written warranty signed by manufacturer agreeing to repair or replace work with finish defects.  “Defects” is defined as peeling, chipping, chalking, fading, abnormal aging or deterioration, and failure to perform as required.

- Warranty Period for Anodized Finish:  1 year from date of shipment from the manufacturer.

- Warranty Period for Powder Coat Finish:  5 years from date of shipment from the manufacturer.

- Warranty Period for Kynar 500 Finish:  5 years from date of shipment from the manufacturer.    (10 and 20 years available if specified).

- Glass Warranty:  Provide written warranty signed by manufacturer agreeing to repair or replace work that has or develops defects in the insulating glass.  “Defects” is defined as seal failure or delamination.

  - Warranty Period for Insulating or Laminated Glass:  5 years from date of Substantial Completion.

(Additional warranty periods may be available if specified.  Consult manufacturer.)

- PRODUCTS

      - MANUFACTURERS

        - Manufacturers:  Subject to compliance with requirements, provide Pinnacle HU 350 or 600 system by Wasco Products, Inc., Wells, ME 04090  (800-388-0293)

        - Substitutions:  Manufacturers shall not be considered without prior approval in writing no later than ten (10) calendar days prior to bid.  Substitute manufacturers must have been in the custom skylight business for not less than a period of 15 years and must submit to the Architect the following:

          - List of similar projects successfully completed within the last five years.

          - Proof of financial capability.

          - Complete details of proposed skylight.

          - Complete specifications for Architect’s review.

      - FRAMING MATERIALS

        - Framing Members:  Extruded aluminum alloy 6063-T6, ASTM B 221 with minimum effective thickness of 0.109 inches.

        - Exterior Pressure Caps: Extruded aluminum alloy 6063-T6, ASTM B 221 with minimum effective thickness of 0.090 inches.

Does Wasco’s have any conceal flashing?

        - Concealed Flashing:  Manufacturer's standard corrosion-resistant, non-staining, non-bleeding flashing; compatible with adjacent materials.

I need some guidance here as to what are Wasco’s standard flashing thicknesses.

        - Exposed Flashing and Closures:  Aluminum sheet alloy and temper of 1100-H14, thickness as require for proper performance.

          - Minimum Thickness:  0.032 inch Apron Flashing.

          - Minimum Thickness:  0.090 inch Closures.

        - Fasteners and Accessories:  Manufacturer's standard corrosion-resistant, non-staining, non-bleeding fasteners and accessories; compatible with adjacent materials.

          - Aluminum-Retaining-Cap Fasteners and Framing Members Fasteners:  ASTM A 193/A 193M, Series 300 stainless-steel screws; type as recommended by manufacturer.

          - Connections to Supporting Structure:  Series 300 Stainless Steel or ASTM A 307, hot dipped galvanized steel fasteners.

        - Framing-System Sealants: Single-component, non-sag, high performance, non-priming, gun-grade elastomeric polyurethane sealant furnished by skylight manufacturer.

          - Sealant complies with ASTM C920, Type S, Grade NS, Class 25, Use T, NT, M, A, G, and O. Canadian Specification CAN/CGSB-19.13-M87, ClassificationMCG-2-25-A-N.

          - Sealant conforms to USDA approval standards.

          - Color: Gray or Dark Bronze.

        - Bituminous Paint:  Cold-applied asphalt mastic paint complying with SSPC-Paint 12, except containing no asbestos, and formulated for 30-mil thickness per coat.

      - GLAZING MATERIALS (EDIT AS REQUIRED)

The paragraph below is the manufacturers standard.  Other custom glazing options are available. Consult with a Wasco representative for non-standard options.  Revise paragraph to suit Project.

Are there any other typical options you want to list here?

        - Insulating Glass:  1-5/16 inch consisting of 1/4 inch tempered exterior lite, 1/2 inch sealed air space and 9/16 inch heat strengthened laminated safety glass interior lite with .090 SGP interlayer. (See Section 08800 for glass performance requirements)

Include the paragraph below when vertical glazed ends are required.  Other custom glazing options are available. Consult with a Wasco representative for non-standard options.  Revise paragraph to suit Project.

        - Laminated Glass: 9/16 inch heat strengthened laminated safety glass interior lite with .090 SGP interlayer.   (See Section 08800 for glass performance requirements)

        - Glazing Gaskets:  1/4” x 5/8” medium density structural glazing tape that meets AAMA 800-88. Structural glazing tape to be compatible with structural silicone adhesive sealant.

        - Spacers, Edge Blocks, and Setting Blocks:  Manufacturer's standard permanent non-migrating type of elastomer type and hardness selected to comply with requirements. Spacers, Edge Blocks, and Setting Blocks to be extruded thermoplastic elastomer by the skylight manufacturer.

        - Structural Glazing Weatherseal Sealant:  Single component neutral-curing silicone sealant recommended by skylight and sealant manufacturers for this use and furnished by skylight manufacturer.

          - Sealant is capable of withstanding 50 percent movement in both extension and compression (total of 100 percent movement) when tested for adhesion and cohesion under maximum cyclic movement according to ASTM C 719.

          - Sealant complies with ASTM C 920 for Type S, Grade NS, Class 50, Uses NT, G, A, and, as applicable to substrates including other sealants with which it comes in contact, O.

          - Color:  Black.

        - Flashing and Closure Sealant:  Single-component, non-sag, high performance, non-priming, gun-grade elastomeric polyurethane sealant furnished by skylight manufacturer.

          - Sealant complies with ASTM C920, Type S, Grade NS, Class 25, Use T, NT, M, A, G, and O. Canadian Specification CAN/CGSB-19.13-M87, Classification MCG-2-25-A-N.

          - Sealant conforms to USDA approval standards.

          - Color: Gray or Dark Bronze.

The following safety screen is an available option.  Edit to suit Project.

      - FABRICATION

I would like to give some guidance as to what sizes are factory assembled and what sizes are field assembled.

        - Framing Components:  As follows:

          - Factory fit and assemble components, where practical.

          - Fabricate components that, when assembled, will have accurately fitted joints with ends coped or mitered to produce hairline joints free of burrs and distortion.

          - Fabricate components to drain water passing joints and to drain condensation and moisture occurring or migrating within skylight system to the exterior.

          - Fabricate components to accommodate expansion, contraction, and field adjustment, and to provide for minimum clearance and shimming at skylight perimeter.

          - Fabricate components to ensure that glazing is thermally and physically isolated from framing members.

          - Form shapes with sharp profiles, straight and free of defects or deformations, before finishing.

          - Fit and assemble components to greatest extent practicable before finishing.

          - Fit and secure joints by heliarc welding and or mechanical fastening.

          - Reinforce members as required to retain fastener threads.

          - Attach retainer bars with gasketed stainless steel fasteners spaced at a maximum of 6 inches on center.

          - Weld components before finishing and in concealed locations to greatest extent practicable to minimize distortion.

          - Before shipping, shop assemble, mark, and disassemble components that cannot be permanently shop assembled.

          - Ship pressure plates pre-gasketed.

        - Provide continuous aluminum frame with weatherproof splice joints and locked and sealed or fully welded corners.  Locate weep holes in the frame at each rafter connection to drain condensation.

        - Prepare framing to receive anchor and connection devices and fasteners.

Keep the following paragraph when smaller units are factory glazed.  Omit paragraph for larger field assembled units.

      - ALUMINUM FINISHES  (EDIT AS REQUIRED)

- General:  Comply with NAAMM “Metal Finishes Manual” recommendations for application and designations of finishes.

- Finish designations prefixed by AA conform to the system for designations of aluminum finishes established by the Aluminum Association.

  - Mill Finish:  Manufacturer’s standard mill finish.

  - Clear-Anodized Finish, Class I:  AA-C22A41 complying with AAMA 611.

  - Clear-Anodized Finish, Class II: AA-C22A31 complying with AAMA 611.

  - Color –Anodized Finish Class I:  AA-C22A42/A44 complying with AAMA 611.  Color:______________

  - Kynar Fluoropolymer Two-Coat System:  (70% PVDF) complying with AAMA 2605.  Color:______________ (3coat and 4 coat available)

  - Powder Coat High-Performance Architectural Coating: comply with AAMA 2604. Color:______________

- EXECUTION

      - EXAMINATION

        - Examine substrates and conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting skylight performance.

          - Proceed with installation only after unsatisfactory conditions have been corrected.

      - PREPARATION

        - Metal Protection:  As follows:

          - Where aluminum will contact dissimilar metals, protect against galvanic action by painting contact surfaces with primer or by applying sealant or tape recommended by manufacturer for this purpose.

          - Where aluminum will contact concrete or masonry, protect against corrosion by painting contact surfaces with bituminous paint.

          - Where aluminum will contact pressure-treated wood, separate dissimilar materials by methods recommended by manufacturer.

      - INSTALLATION

        - General:  Comply with manufacturer's written instructions for protecting, handling, and installing skylight components.

          - Fit frame joints to produce hairline joints free of burrs and distortion.

          - Rigidly secure non-movement joints.

          - Accommodate thermal and mechanical movements.

          - Install framing components to drain water passing joints and to drain condensation and moisture occurring or migrating within skylight system to the exterior.

          - Coordinate installation of flashings at skylight perimeters to maintain continuity of water barriers.

          - Set continuous frames and flashings in a full sealant bed, unless otherwise indicated.  Comply with requirements in Division 7 Section "Joint Sealants."

        - Erection Tolerances:  Install skylight components true in plane, accurately aligned, and without warp or rack.  Adjust framing to comply with the following tolerances:

          - Variation from Plane:  Limit variation from plane or location shown to 1/8 inch in 10 feet; 1/4 inch over total length.

          - Alignment:  Where surfaces abut in line and at corners and where surfaces are separated by less than 3 inches, limit offset from true alignment to less than 1/32 inch; otherwise, limit offset from true alignment to 1/8 inch.

Delete paragraph below if no field glazing.

        - Field Glazing:  Locate and size extruded elastomeric setting blocks and spacers in accordance with the glazing manufacturer’s recommendations.  At no point shall the glazing come in contact with the skylight frame or fasteners

        - Install secondary-sealant weatherseal according to sealant manufacturer's written instructions to provide weatherproof joints.  Install joint fillers behind sealant as recommended by sealant manufacturer.

Does Wasco ever do any field testing?

      - CLEANING

        - Clean exposed metal and glass surfaces according to manufacturer’s instructions during installation.  Touch up damaged metal coatings.

        - Final cleaning by others.

END OF SECTION 08625